SECTION 15990

TESTING, ADJUSTING, AND BALANCE

BUILDING C

PART 1 GENERAL

1.01	RELATED DOCUMENTS

A.	Drawings and general provisions of Contract, including General and Supplementary Conditions and Division 1 Specification sections, apply to this section.

1.02	SUMMARY

A.	This section specifies the requirements and procedures for total mechanical systems testing, adjusting, and balancing. Requirements include measurement and establishment of the fluid quantities of the mechanical system as required to meet design specifications, and recording and reporting the results.

1.04	QUALITY ASSURANCE

A.	Agency Qualifications

1.	The independent testing, adjusting, and balancing agency certified by National Environmental Balancing Bureau (NEBB) in the  disciplines required for this project. Services shall include, measurement and establishment of the fluid quantities of the mechanical systems as required to meet design specifications, and recording and reporting the results.

B.	Code and Standards

1.	NEBB: Current Edition of “Procedural Standards for Testing, Adjusting, and Balancing of Environmental Systems”

2.	American Society of Heating, Refrigeration, and Air-Conditioning Engineers (ASHRAE): ASHRAE handbook, HVAC Applications Volume, Chapter 36, Testing, Adjusting, and Balancing.

PART 2   PROJECT SPECIFIC EXECUTION

3.01	SCOPE OF WORK

A.	TAB services to be provided on the following:

1.	AHU-1 and associated VAV’s and Fan Terminal Units.

2.	Air balance NEW fan coil units FCU-6, FCU-7, and FCU-8 (hydronic coil test report – not required)

3.	All sidewall diffusers to be measured with a high quality, calibrated anemometer instrument.

4.	Water balance chilled water hydronic loop.

3.02	PRELIMINARY PROCEDURES FOR SYSTEM BALANCING

A.	Before operating the system, perform these steps:

1..	Obtain design drawings and specifications and become thoroughly acquainted with the design intent.

2.	Compare design to installed equipment and field installations.

3.	Prepare NEBB report test sheets to correlate with TAB scope of work. Include information regarding all terminal devices (air terminal units, GRD’s, circuit balance valves, and coils). Obtain manufacture’s outlet factors and recommended procedures for testing.

4.	Determine best locations in ductwork for most accurate duct traverses. Duct traverses shall be performed for minimum outside air quantities for all air moving systems except fan coil units.

3.03	MEASUREMENTS

A.	Provide all required instrumentation to obtain proper measurements, calibrated to the tolerances specified in the referenced standards. Instruments shall meet the specifications of the referenced standards and be applied only as recommended by the manufacturer.

3.04	PERFORMING TESTING, ADJUSTING, AND BALANCING

A.	Perform testing and balancing procedures on each system identified in the scope of work and in accordance with the procedures outlined in the referenced standards.

B.	Mark equipment setting, including damper control positions, valve indictors, fan speed control levers, and similar controls and devices, to show final settings. Mark with paint or other suitable, permanent identification materials.

3.05	RECORD AND REPORT DATA

A.	Record all data obtained during testing, adjusting, and balancing in accordance with, and on NEBB forms.

B.	Prepare report of recommendations for correcting unsatisfactory mechanical performances when systems cannot be successfully balanced.

END OF SECTION